## Sheet1
[7 empty] | AS/NZS 4130 - Pressure Pipe - Dimensions and Weights | [16 empty] | Rev | 0
PN | 4 |  |  | 6.3 |  |  | 8 |  |  | 10 |  |  | 12.5 |  |  | 16 |  |  | 20 |  |  | 25 |  |  | PN
SDR | 41 |  |  | 26 |  |  | 21 |  |  | 17 |  |  | 13.6 |  |  | 11 |  |  | 9 |  |  | 7.4 |  |  | SDR
Outer Diameter (mm) | Min Wall Thickness (mm) | Mean ID (mm) | Weight Avg (kg/m) | Min Wall Thickness (mm) | Mean ID (mm) | Weight Avg (kg/m) | Min Wall Thickness (mm) | Mean ID (mm) | Weight Avg (kg/m) | Min Wall Thickness (mm) | Mean ID (mm) | Weight Avg (kg/m) | Min Wall Thickness (mm) | Mean ID (mm) | Weight Avg (kg/m) | Min Wall Thickness (mm) | Mean ID (mm) | Weight Avg (kg/m) | Min Wall Thickness (mm) | Mean ID (mm) | Weight Avg (kg/m) | Min Wall Thickness (mm) | Mean ID (mm) | Weight Avg (kg/m) | Outer Diameter (mm)
16 | [15 empty] | 1.6 | 12.7 | 0.08 | 1.8 | 12.3 | 0.08 | 2.2 | 11.4 | 0.1 | 16
20 | [12 empty] | 1.6 | 16.7 | 0.1 | 1.9 | 16 | 0.11 | 2.3 | 15.2 | 0.13 | 2.8 | 14.2 | 0.16 | 20
25 | [8 empty] | 1.6 |  | 21.7 | 0.12 | 1.9 | 21 | 0.14 | 2.3 | 20.2 | 0.17 | 2.8 | 19.2 | 0.2 | 3.5 | 17.7 | 0.24 | 25
32 | [5 empty] | 1.6 |  | 28.7 | 0.16 | 1.9 | 28 | 0.19 | 2.4 | 27 | 0.23 | 2.9 | 26 | 0.27 | 3.6 | 24.5 | 0.33 | 4.4 | 22.8 | 0.39 | 32
40 | [5 empty] | 1.9 |  | 36.1 | 0.24 | 2.4 | 35 | 0.3 | 3 | 33.8 | 0.36 | 3.7 | 32.3 | 0.43 | 4.5 | 30.6 | 0.52 | 5.5 | 28.5 | 0.61 | 40
50 | [5 empty] | 2.4 |  | 45 | 0.38 | 3 | 43.9 | 0.46 | 3.7 | 42.4 | 0.55 | 4.6 | 40.4 | 0.67 | 5.6 | 38.4 | 0.8 | 6.9 | 35.7 | 0.95 | 50
63 |  |  | 2.4 |  | 58.1 | 0.48 | 3 | 56.9 | 0.58 | 3.8 | 55.2 | 0.73 | 4.7 | 53.3 | 0.88 | 5.8 | 51 | 1.07 | 7.1 | 48.2 | 1.28 | 8.6 | 45.1 | 1.5 | 63
75 |  |  | 2.9 |  | 69.2 | 0.68 | 3.6 | 67.7 | 0.83 | 4.5 | 65.8 | 1.03 | 5.5 | 63.7 | 1.23 | 6.8 | 61 | 1.49 | 8.4 | 57.6 | 1.79 | 10.3 | 53.6 | 2.13 | 75
90 |  |  | 3.5 |  | 83 | 0.99 | 4.3 | 81.3 | 1.2 | 5.4 | 79 | 1.48 | 6.6 | 76.5 | 1.77 | 8.2 | 73 | 2.16 | 10.1 | 69.1 | 2.59 | 12.3 | 64.5 | 3.05 | 90
110 | 2.7 | 104.7 | 0.95 | 4.3 | 101.3 | 1.48 | 5.3 | 99.2 | 1.8 | 6.6 | 96.5 | 2.2 | 8.1 | 93.3 | 2.66 | 10 | 89.4 | 3.2 | 12.3 | 84.5 | 3.84 | 15.1 | 78.6 | 4.57 | 110
125 | 3.1 | 118.9 | 1.24 | 4.8 | 115.4 | 1.86 | 6 | 112.9 | 2.3 | 7.4 | 109.9 | 2.8 | 9.2 | 106.1 | 3.42 | 11.4 | 101.5 | 4.15 | 14 | 96.1 | 4.96 | 17.1 | 89.5 | 5.88 | 125
140 | 3.5 | 133.2 | 1.56 | 5.4 | 129.2 | 2.35 | 6.7 | 126.5 | 2.87 | 8.3 | 123 | 3.52 | 10.3 | 118.9 | 4.29 | 12.7 | 113.9 | 5.17 | 15.7 | 107.6 | 6.23 | 19.2 | 100.2 | 7.39 | 140
160 | 4 | 152.3 | 2.02 | 6.2 | 147.6 | 3.08 | 7.7 | 144.5 | 3.77 | 9.5 | 140.7 | 4.59 | 11.8 | 135.9 | 5.6 | 14.6 | 130 | 6.78 | 17.9 | 123 | 8.11 | 21.9 | 114.7 | 9.62 | 160
180 | 4.4 | 171.5 | 2.51 | 6.9 | 166.3 | 3.84 | 8.6 | 163.1 | 4.74 | 10.7 | 158.3 | 5.81 | 13.3 | 152.8 | 7.1 | 16.4 | 146.3 | 8.58 | 20.1 | 138.5 | 10.26 | 24.6 | 129.1 | 12.16 | 180
200 | 4.9 | 190.5 | 3.08 | 7.7 | 184.6 | 4.76 | 9.6 | 180.6 | 5.87 | 11.9 | 175.8 | 7.16 | 14.7 | 170 | 8.71 | 18.2 | 162.5 | 10.57 | 22.4 | 153.7 | 12.68 | 27.3 | 143.4 | 15 | 200
225 | 5.5 | 214.4 | 3.9 | 8.6 | 207.9 | 5.98 | 10.8 | 203.3 | 7.42 | 13.4 | 197.8 | 9.09 | 16.6 | 191 | 11.06 | 20.5 | 182.9 | 13.39 | 25.1 | 173.2 | 16 | 30.8 | 161.3 | 19.02 | 225
250 | 6.2 | 238 | 4.89 | 9.6 | 230.9 | 7.41 | 11.9 | 226 | 9.08 | 14.8 | 220 | 11.14 | 18.4 | 212.4 | 13.63 | 22.7 | 203.4 | 16.46 | 27.9 | 192.5 | 19.73 | 34.2 | 179.2 | 23.48 | 250
280 | 6.9 | 266.7 | 6.06 | 10.7 | 258.7 | 9.25 | 13.4 | 253 | 11.46 | 16.6 | 246.3 | 13.99 | 20.6 | 237.9 | 17.08 | 25.4 | 227.8 | 20.64 | 31.3 | 215.4 | 24.8 | 38.3 | 200.7 | 29.44 | 280
315 | 7.7 | 300.2 | 7.62 | 12.1 | 290.9 | 11.78 | 15 | 284.9 | 14.4 | 18.7 | 276.6 | 17.72 | 23.2 | 267.6 | 21.64 | 28.6 | 256.3 | 26.13 | 35.2 | 242.4 | 31.38 | 43 | 226.1 | 37.16 | 315
355 | 8.7 | 338.2 | 9.69 | 13.6 | 327.9 | 14.88 | 16.9 | 321 | 18.28 | 21.1 | 312.1 | 22.55 | 26.1 | 301.6 | 27.43 | 32.2 | 288.8 | 33.16 | 39.6 | 273.3 | 39.76 | 48.5 | 254.6 | 47.24 | 355
400 | 9.8 | 380 | 12.28 | 15.3 | 369.5 | 18.88 | 19.1 | 361.5 | 23.31 | 23.7 | 351.9 | 28.5 | 29.4 | 339.9 | 34.79 | 36.3 | 325.4 | 42.1 | 44.7 | 307.8 | 50.55 | 54.6 | 287 | 59.92 | 400
450 | 11 | 428.9 | 15.49 | 17.2 | 415.8 | 23.87 | 21.5 | 406.8 | 29.48 | 26.7 | 395.9 | 36.11 | 33.1 | 382.4 | 44.07 | 40.9 | 366.1 | 53.31 | 50.2 | 346.5 | 63.9 | 61.5 | 322.8 | 75.92 | 450
500 | 12.3 | 476.3 | 19.28 | 19.1 | 462 | 29.45 | 23.9 | 452 | 36.37 | 29.6 | 439.9 | 44.48 | 36.8 | 424.9 | 54.38 | 45.4 | 406.8 | 65.78 | 55.8 | 385 | 48.86 |  |  |  | 500
560 | 13.7 | 533.6 | 24 | 21.4 | 517.4 | 36.91 | 26.7 | 506.4 | 45.52 | 33.2 | 492.7 | 55.89 | 41.2 | 475.8 | 68.22 | 50.8 | 455.8 | 82.4 | 62.5 | 430.3 | 98.93 |  |  |  | 560
630 | 15.4 | 600.4 | 30.37 | 24.1 | 582.1 | 46.77 | 30 | 569.8 | 57.5 | 37.3 | 554.4 | 70.62 | 46.3 | 535.5 | 86.23 | 57.2 | 512.6 | 104.42 | 70.3 | 484.1 | 125.2 |  |  |  | 630
710 | 17.4 | 676.5 | 38.65 | 27.2 | 655.9 | 59.45 | 33.9 | 641.9 | 73.22 | 42.1 | 624.6 | 89.82 | 52.2 | 603.4 | 109.55 | 64.5 | 577.6 | 132.64 | 79.3 | 546.5 | 159.13 |  |  |  | 710
800 | 19.6 | 762.3 | 49.01 | 30.6 | 739.2 | 75.29 | 38.1 | 723.4 | 92.8 | 47.4 | 703.9 | 113.89 | 58.8 | 680 | 138.96 | 72.5 | 651 | 168.11 | 89.3 | 615.9 | 201.9 |  |  |  | 800
900 | 22 | 857.8 | 61.81 | 34.4 | 831.7 | 95.23 | 42.9 | 813.9 | 117.42 | 53.5 | 791.7 | 144.55 | 66.2 | 764.9 | 176.04 | 81.7 | 732.4 | 212.91 | [6 empty] | 900
1000 | 24.5 | 952.9 | 76.54 | 38.2 | 924.1 | 117.5 | 47.7 | 904.2 | 145.07 | 59.3 | 879.8 | 178.06 | 72.5 | 852.1 | 214.41 | 90.3 | 814.9 | 261.4 | [6 empty] | 1000
1200 | 29.4 | 1143.1 | 110.14 | 45.9 | 1108.5 | 169.18 | 57.2 | 1084.7 | 208.73 | 67.9 | 1062.7 | 245.17 | 88.2 | 1020 | 312.54 | [9 empty] | 1200
1400 | 34.4 | 1332.6 | 150.19 | 53.2 | 1293.1 | 239.54 | 66.7 | 1266.1 | 283.64 | 82.4 | 1233.1 | 346.07 | [12 empty] | 1400
1600 | 39.3 | 1522.3 | 195.75 | 61.3 | 1476.1 | 300.95 | 76.2 | 1447 | 370.23 | 94.1 | 1409.4 | 451.49 | [12 empty] | 1600
1800 | 43.8 | 1716 |  | 69.1 | 1662.8 |  | 85.7 | 1628 | 468.94 | [15 empty] | 1800
2000 | 48.8 | 1906.4 |  | 76.9 | 1847.4 |  | 95.2 | 1808.9 | 578.91 | [15 empty] | 2000
Note: No guarantee of accuracy, confirm dimensions with other sources.